CHECKLIST: INDUCED FLOW FAN CATALOGS

CATALOG IDENTIFICATION_______________________  DATE OF CATALOG___________________

Note:  Please reference your completed CRP Form to determine which selections are appropriate.

I.   SEAL USAGE IN CATALOGS

1. Pick the correct AMCA Seal: [check all that apply]

Efficiency Air Performance

Efficiency Sound and Air Performance

Induced Flow Fan Air Performance

Induced Flow Fan Air and Sound Performance

2. Placement of AMCA Seal: [check all that apply]

If the catalog contains all licensed products, the seal and qualifying statement shall be prominently displayed either on the cover or in the catalog.

If the catalog contains both licensed and unlicensed products, the AMCA Seal and qualifying statement shall not be shown on the outside cover.

II.   QUALIFYING STATEMENT ADJACENT TO THE SEAL

In catalogs containing ratings of licensed products, the following statement shall be printed prominently and immediately adjacent to the reproduction of the AMCA Certified Ratings Seal:

"(Licensee's name as shown on License Agreement) certifies that the (product description) shown herein is (or are) licensed to bear the AMCA Seal.  The ratings shown are based on tests and procedures performed in accordance with AMCA Publication 211 (and AMCA Publication 311 if sound is also certified) and comply with the requirements of the AMCA Certified Ratings Program."

III.  CATALOG IDENTIFICATION REQUIREMENTS

Catalogs containing performance ratings of licensed products shall have a catalog identification reference (e.g. Catalog No. XXX Rev. 1), and unabbreviated current catalog date, (e.g. November 2004) on the outside front or back cover.

Where ratings are on separate sheets or on loose leaf that may be removed from the cover, each sheet or loose leaf shall be identified and dated as above.

IV.  EFFICIENCY

The following statement shall be shown immediately adjacent to the efficiency ratings:

Efficiency ratings are fan static (or fan total) and include (or exclude) bearing and/or Power Transmission Losses.

V.  REQUIREMENTS FOR AIR PERFORMANCE

1.  Duct Statement (Installation Type Testing Method)

Installation Method [this is different from the rating method; see test report for installation method; check one]

For all rating methods, one of the following statements shall be shown immediately adjacent to the rating tables, graphs and charts:

A		Performance certified is for installation type A – Free inlet, Free outlet.

B		Performance certified is for installation type B – Free inlet, Ducted outlet.

C		Performance certified is for installation type C – Ducted inlet, Free outlet.

D		Performance certified is for installation type D – Ducted inlet, Ducted outlet.

A & C	Performance certified is for installation type A & C – Free or ducted inlet, Free outlet.

B & D	Performance certified is for installation type B & D – Free or ducted inlet, Ducted outlet.

2.  Rating Method “L” (Induced Flow Fans)

The performance ratings for each model number shall include:

Inlet airflow rate

Fan static pressure

Fan input power

Impeller speed

Inlet air density (if other than standard air)

Fan static efficiency (optional)

Outlet airflow rate

Outlet area (defined as the outlet area of the windband)

Nozzle velocity (Inlet airflow rate divided by nozzle discharge area)

Required Statements:

Power rating (watts, kW, or bhp) does not include transmission losses.

Performance ratings do not include the effects of cross winds.

Performance ratings do not include the effects of appurtenances (accessories).

Or

Performance ratings include the effects of [list appurtenances here]:

VI.  ADDITIONAL REQUIREMENTS FOR INDUCED FLOW FANS

When electrical input power is cataloged, the tested motor shall be operated at the catalog voltage and frequency, or where a voltage range is stated, it shall be the mean voltage.

In addition, the temperature of the motor winding has to be stable for each tested operating point.